## cost_matrix
| label | costs_total | costs_om_total | costs_investment_over_lifetime | costs_upfront_in_year_zero | Replacement_costs_during_project_lifetime | costs_dispatch | costs_cost_om | annuity_total | annuity_om | levelized_cost_of_energy_of_asset
0 | DSO_consumption | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | DSO_feedin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | pv_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | pv_frei | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | pv_wasser | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | wind_erweiterung | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | wind_karholz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | wind_winnberg03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | wind_winnberg04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Electricity_grid_DSO_consumption_period | 6055209.7257 | 6055209.7257 | 0 | 0 | 0 | 0 | 6055209.7257 | 527920.7773 | 527920.7773 | 0.08862
0 | PV_Frei | 4213915.1662 | 986887.1447 | 3227028.0215 | 3441652.74 | -214624.7185 | 0 | 986887.1447 | 367388.3269 | 86041.3185 | 0.05025
0 | PV_Halle 18 | 155582.8331 | 178930.771 | -23347.9379 | 0 | -23347.9379 | 0 | 178930.771 | 13564.4204 | 15600 | 0.02069
0 | PV_Wasser | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Wind_Erweiterung | 598456.4538 | 0 | 598456.4538 | 667871.631 | -69415.1772 | 0 | 0 | 52176.1608 | 0 | 0.03491
0 | Wind_Karholz | -286860.3487 | 0 | -286860.3487 | 0 | -286860.3487 | 0 | 0 | -25009.7924 | 0 | -0.00324
0 | Wind_Winnberg 03 | -325108.3952 | 0 | -325108.3952 | 0 | -325108.3952 | 0 | 0 | -28344.4314 | 0 | -0.00383
0 | Wind_Winnberg 04 | -305984.372 | 0 | -305984.372 | 0 | -305984.372 | 0 | 0 | -26677.1119 | 0 | -0.0033
0 | Electricity_grid_DSO_consumption_source | 11273673.7986 | 11273673.7986 | 0 | 0 | 0 | 11273673.7986 | 0 | 982890.2556 | 982890.2556 | 0.165
0 | Industriepark | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | AC bus_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | DC bus 18_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | DC bus frei_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | DC bus wasser_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | DSO bus_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | wind bus erweiterung_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | wind bus karholz_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | wind bus winnberg 03_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | wind bus winnberg 04_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Electricity_grid_DSO_feedin_sink_sink | -3913884.7488 | -3913884.7488 | 0 | 0 | 0 | -3913884.7488 | 0 | -341230.3079 | -341230.3079 | -0.02

## scalar_matrix
| label | unit | installedCap | optimizedAddCap | total_flow | annual_total_flow | peak_flow | average_flow | Total emissions
0 | DSO_consumption | kVA | 0 | 5580.5579 | 5956910.6402 | 5956910.6402 | 5580.5579 | 680.0126
0 | DSO_feedin | kVA | 0 | 13221.139 | 17061515.394 | 17061515.394 | 13221.139 | 1947.6616
0 | pv_18 | kVA | 0 | 519 | 655690.5 | 655690.5 | 519 | 74.8505
0 | pv_frei | kVA | 0 | 5736.0879 | 7311277.0728 | 7311277.0728 | 5736.0879 | 834.6207
0 | pv_wasser | kVA | 0 | 0 | 0 | 0 | 0 | 0
0 | wind_erweiterung | kVA | 0 | 580.7579 | 1494588.1278 | 1494588.1278 | 580.7579 | 170.6151
0 | wind_karholz | kVA | 0 | 3000 | 7720539.0591 | 7720539.0591 | 3000 | 881.3401
0 | wind_winnberg03 | kVA | 0 | 3400 | 7399537.2487 | 7399537.2487 | 3400 | 844.696
0 | wind_winnberg04 | kVA | 0 | 3200 | 8086536.6619 | 8086536.6619 | 3200 | 923.1206
0 | Electricity_grid_DSO_consumption_period | ? | 0 | 5580.5579 | 5956910.6402 | 5956910.6402 | 5580.5579 | 680.0126
0 | PV_Frei | kWp | 0 | 5736.0879 | 7311277.0728 | 7311277.0728 | 5736.0879 | 834.6207 | 0
0 | PV_Halle 18 | kWp | 780 | 0 | 655690.5 | 655690.5 | 519 | 74.8505 | 0
0 | PV_Wasser | kWp | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Wind_Erweiterung | kW | 0 | 580.7579 | 1494588.1278 | 1494588.1278 | 580.7579 | 170.6151 | 0
0 | Wind_Karholz | kW | 3000 | 0 | 7720539.0578 | 7720539.0578 | 3000 | 881.3401 | 0
0 | Wind_Winnberg 03 | kW | 3400 | 0 | 7399537.2456 | 7399537.2456 | 3400 | 844.696 | 0
0 | Wind_Winnberg 04 | kW | 3200 | 0 | 8086536.6634 | 8086536.6634 | 3200 | 923.1206 | 0
0 | Electricity_grid_DSO_consumption_source | ? | 0 | 5580.5579 | 5956910.6402 | 5956910.6402 | 5580.5579 | 680.0126 | 2382764.2561
0 | Industriepark | kW | 0 | 0 | 21563563.912 | 21563563.912 | 5749.52 | 2461.5941
0 | AC bus_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | DC bus 18_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | DC bus frei_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | DC bus wasser_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | DSO bus_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | wind bus erweiterung_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | wind bus karholz_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | wind bus winnberg 03_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | wind bus winnberg 04_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | Electricity_grid_DSO_feedin_sink_sink | ? | 0 | 13221.139 | 17061515.394 | 17061515.394 | 13221.139 | 1947.6616

## scalars
| 0 | unit
costs_total | 17465000.1127 | EUR
costs_om_total | 14580816.6913 | EUR
costs_investment_over_lifetime | 2884183.4214 | EUR
costs_upfront_in_year_zero | 4109524.371 | EUR
Replacement_costs_during_project_lifetime | -1225340.9496 | NA
costs_dispatch | 7359789.0498 | EUR
costs_cost_om | 7221027.6415 | EUR
annuity_total | 1522678.2974 | EUR/year
annuity_om | 1271222.0436 | EUR/year
Total_demandElectricity | 21563563.912 | NA
Total_demandElectricity_electricity_equivalent | 21563563.912 | NA
Total_demand_electricity_equivalent | 21563563.912 | NA
Total_excessElectricity | -5.3454e-12 | NA
Total_excessElectricity_electricity_equivalent | -5.3454e-12 | NA
Total_excess_electricity_equivalent | -5.3454e-12 | NA
Total_feedinElectricity | 17061515.394 | NA
Total_feedinElectricity_electricity_equivalent | 17061515.394 | NA
Total_feedin_electricity_equivalent | 17061515.394 | NA
Attributed costsElectricity | 17465000.1127 | NA
Levelized costs of electricity equivalentElectricity | 0.070613 | NA
Levelized costs of electricity equivalent | 0.070613 | NA
Total internal renewable generation | 32668168.6673 | NA
Total internal non-renewable generation | 0 | NA
Total renewable energy use | 35229640.2426 | NA
Total non-renewable energy use | 3395439.0649 | NA
Total internal generation | 32668168.6673 | NA
Renewable share of local generation | 1 | NA
Renewable factor | 0.91209 | NA
Onsite energy fraction | 0.47773 | NA
Onsite energy matching | 0.72375 | NA
Degree of autonomy | 1.515 | NA
Total emissions | 2382764.2561 | NA
Specific emissions per electricity equivalent | 0.1105 | NA

## KPI individual sectors
Electricity
Renewable factor | 0.91209
Renewable share of local generation | 1
Total internal non-renewable generation | 0
Total internal non-renewable generation_electricity_equivalent | 0
Total internal renewable generation | 32668168.6673
Total internal renewable generation_electricity_equivalent | 32668168.6673
Total non-renewable energy use | 3395439.0649
Total non-renewable energy use_electricity_equivalent | 3395439.0649
Total renewable energy use | 35229640.2426
Total renewable energy use_electricity_equivalent | 35229640.2426